## Sheet1
|  |  | MFIA PANEL SCHEDULE | [5 empty] | 2026-07-29 08:58 | [5 empty] | 0 | 0 | 0 | Print panel schedules on stick-on | Save a panel schedule to drive A | Load a panel schedule from drive A | Load a blank 3 phase panel schedule | Load a blank 1 phase panel schedule | Print 2 panel schedules on 8.5"x11" paper | Return to Symphony menu system
| panel |  | mounting |  |  | location |  |  | connected load amps | [5 empty] | 0 | 0 | 0 |  | {SERVICES}FS{ESCAPE} | {SERVICES}FR | {SERVICES}FRPNLSCHED.WR1~ | {SERVICES}FRSINGLEP.WR1~ | pssrv1..ap47~qagpq
| PANEL 'L2' |  | SURFACE | [5 empty] | 74.5331 | [5 empty] | 5340 | 3420 | 4500
| voltage |  | phase |  |  | bus & main |  |  | calculated load amps | [5 empty] | 2160 | 2340 | 2520
| 208Y/120V |  | 3 |  |  | 225A MLO |  |  | 60.249 | [5 empty] | 0 | 0 | 0
C | service | va | a/p | no. | a b c | no. | a/p | va | service | C |  |  |  |  | 0 | 0 | 0
2 | RECEPT.-CORRIDOR | 1080 | 20/1 | 1 | * | 2 | 20/1 | 720 | RECEPTACLES | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0
2 | RECEPT.-CORRIDOR | 1080 | 20/1 | 3 | * | 4 | 20/1 | 720 | RECEPTACLES | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0
2 | RECEPTACLES | 1440 | 20/1 | 5 | * | 6 | 20/1 | 900 | RECEPTACLES | 2 | 1 | 0 | 1 | 0 | 1200 | 1700 | 1200
2 | RECEPTACLES | 720 | 20/1 | 7 | * | 8 | 20/1 | 720 | RECEPTACLES | 2 | 1 | 0 | 1 | 0 | 540 | 720 | 540
2 | RECEPTACLES | 720 | 20/1 | 9 | * | 10 | 20/1 | 720 | PROCEDURE TABLE | 5 | 1 | 0 | 1 | 0 | 0 | 0 | 0
2 | RECEPTACLES | 720 | 20/1 | 11 | * | 12 | 20/1 | 540 | RECEPTACLES-PROCED. | 5 | 1 | 0 | 1 | 0 | 640 | 0 | 0
2 | RECEPTACLES | 720 | 20/1 | 13 | * | 14 | 20/1 | 540 | RECEPTACLES-PROCED. | 5 | 1 | 0 | 1 | 0 | 0 | 0 | 0
2 | RECEPTACLES | 720 | 20/1 | 15 | * | 16 | 20/1 | 720 | RECEPTACLES | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0
2 | RECEPTACLES | 720 | 20/1 | 17 | * | 18 | 20/1 | 900 | RECEPTACLES | 2 | 1 | 0 | 1 | 0
2 | RECEPTACLES | 900 | 20/1 | 19 | * | 20 | 20/1 | 720 | RECEPTACLES | 2 | 1 | 0 | 1 | 0
5 | REFRIGERATOR | 500 | 20/1 | 21 | * | 22 | 20/1 | 900 | RECEPTACLES | 2 | 1 | 0 | 1 | 0
5 | COFFEE BAR | 1200 | 20/1 | 23 | * | 24 | 20/1 | 720 | RECEPTACLES | 2 | 1 | 0 | 1 | 0
5 | COFFEE BAR | 1200 | 20/1 | 25 | * | 26 | 20/1 |  | SPARE |  | 1 | 0 | 1 | 0
5 | COFFEE BAR | 1200 | 20/1 | 27 | * | 28 | 20/1 |  | SPARE |  | 1 | 0 | 1 | 0
2 | RECEPTACLES | 900 | 20/1 | 29 | * | 30 | 20/1 |  | SPARE |  | 1 | 0 | 1 | 0
2 | RECEPTACLES | 720 | 20/1 | 31 | * | 32 | 20/1 | 640 | WH-1, P-1 & IAC-1 | 6 | 1 | 0 | 1 | 0
2 | RECEPTACLES | 900 | 20/1 | 33 | * | 34 | 20/1 |  | SPARE |  | 1 | 0 | 1 | 0
2 | RECEPTACLES | 720 | 20/1 | 35 | * | 36 | 20/1 |  | SPARE |  | 1 | 0 | 1 | 0
2 | RECEPTACLES | 1200 | 20/1 | 37 | * | 38 |  |  | SPACE ONLY |  | 1 | 0 | 0 | 0
| SPARE |  | 20/1 | 39 | * | 40 |  |  | SPACE ONLY |  | 1 | 0 | 0 | 0
| SPARE |  | 20/1 | 41 | * | 42 |  |  | SPACE ONLY |  | 1 | 0 | 0 | 0
| Phase A | 9880 | VA |  |  | NOTES: |  |  | line-line voltage |  |  | 0 |  | 0
| Phase B | 8180 | VA | [5 empty] | 208 |  |  | 1
| Phase C | 8760 | VA | [5 empty] | largest motor (va)
| Total Connected | 26820 | VA | [5 empty] | 0
| load code: | ph. A | ph. B |  | ph. C |  | total | factor | calculated load (va)
| 1. LIGHTS= | 0 | 0 |  | 0 | VA | 0 | 1.25 | 0
| 2. RECEPT.= | 7500 | 5760 |  | 7020 | VA | 20280 | 1 + 0.5 | 15140
| 3. HEATING= | 0 | 0 |  | 0 | VA | 0 | 1 | 0
| 4. KITCHEN= | 0 | 0 |  | 0 | VA | 0 | 1 | 0
| 5. EQUIP.= | 1740 | 2420 |  | 1740 | VA | 5900 | 1 | 5900
| 6. MOTORS= | 640 | 0 |  | 0 | VA | 640 | * | 640
| 7. MISC= | 0 | 0 |  | 0 | VA | 0 | 1 | 0
| (* 125% of the largest motor + 100% of the balance) | [6 empty] | TOTAL = | 21680
PANEL 'L2' | 0 | 20280 | 0 | 0 | 5900 | 640 | 0