## Sheet1
|  |  | MFIA PANEL SCHEDULE | [5 empty] | 2026-07-29 05:44 | [5 empty] | 0 | 0 | 0 | Print panel schedules on stick-on | Save a panel schedule to drive A | Load a panel schedule from drive A | Load a blank 3 phase panel schedule | Load a blank 1 phase panel schedule | Print 2 panel schedules on 8.5"x11" paper | Return to Symphony menu system
| panel |  | mounting |  |  | location |  |  | connected load amps | [5 empty] | 0 | 0 | 0 |  | {SERVICES}FS{ESCAPE} | {SERVICES}FR | {SERVICES}FRPNLSCHED.WR1~ | {SERVICES}FRSINGLEP.WR1~ | pssrv1..ap47~qagpq
| PANEL 'L3' |  | SURFACE | [5 empty] | 37.7946 | [5 empty] | 0 | 0 | 0
| voltage |  | phase |  |  | bus & main |  |  | calculated load amps | [5 empty] | 720 | 720 | 720
| 208Y/120V |  | 3 |  |  | 225A MLO |  |  | 37.7946 | [5 empty] | 0 | 0 | 0
C | service | va | a/p | no. | a b c | no. | a/p | va | service | C |  |  |  |  | 0 | 0 | 0
5 | PAGING SYS. | 500 | 20/1 | 1 | * | 2 | 20/1 | 720 | RECEPTACLES, EF-6 | 6 | 1 | 0 | 1 | 0 | 0 | 0 | 0
5 | FIRE ALARM PANEL | 500 | 20/1 | 3 | * | 4 | 20/1 | 1200 | RECEPTACLES | 5 | 1 | 0 | 1 | 0 | 0 | 0 | 0
5 | NURSE CALL SYSTEM | 500 | 20/1 | 5 | * | 6 | 20/1 | 1200 | RECEPTACLES | 5 | 1 | 0 | 1 | 0 | 2940 | 2940 | 2440
5 | SECURITY SYSTEM | 500 | 20/1 | 7 | * | 8 | 20/1 | 720 | RECEPTACLES | 2 | 1 | 0 | 1 | 0 | 0 | 1200 | 1200
5 | RECEPT.-DATA ROOM | 500 | 20/1 | 9 | * | 10 | 20/1 | 720 | RECEPTACLES | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0
5 | RECEPT.-DATA ROOM | 500 | 20/1 | 11 | * | 12 | 20/1 | 720 | RECEPTACLES | 2 | 1 | 0 | 1 | 0 | 720 | 0 | 0
5 | RECEPT.-DATA ROOM | 500 | 20/1 | 13 | * | 14 | 20/1 |  | SPARE |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
5 | RECEPT.-DATA ROOM | 500 | 20/1 | 15 | * | 16 | 20/1 |  | SPARE |  | 1 | 0 | 1 | 0 | 0 | 0 | 0
5 | RECEPT.-EXAM 'EMR' | 720 | 20/1 | 17 | * | 18 | 20/1 |  | SPARE |  | 1 | 0 | 1 | 0
5 | RECEPT.-EXAM 'EMR' | 720 | 20/1 | 19 | * | 20 | 20/1 |  | SPARE |  | 1 | 0 | 1 | 0
5 | RECEPT.-EXAM 'EMR' | 720 | 20/1 | 21 | * | 22 | 20/1 |  | SPARE |  | 1 | 0 | 1 | 0
5 | RECEPT.-EXAM 'EMR' | 720 | 20/1 | 23 | * | 24 | 20/1 |  | SPARE |  | 1 | 0 | 1 | 0
5 | RECEPT.-EXAM 'EMR' | 720 | 20/1 | 25 | * | 26 | 20/1 |  | SPARE |  | 1 | 0 | 1 | 0
5 | RECEPT.-EXAM 'EMR' | 720 | 20/1 | 27 | * | 28 | 20/1 |  | SPARE |  | 1 | 0 | 1 | 0
| SPARE |  | 20/1 | 29 | * | 30 | 20/1 |  | SPARE |  | 1 | 0 | 1 | 0
| SPACE ONLY |  |  | 31 | * | 32 |  |  | SPACE ONLY |  | 0 | 0 | 0 | 0
| SPACE ONLY |  |  | 33 | * | 34 |  |  | SPACE ONLY |  | 0 | 0 | 0 | 0
| SPACE ONLY |  |  | 35 | * | 36 |  |  | SPACE ONLY |  | 0 | 0 | 0 | 0
| SPACE ONLY |  |  | 37 | * | 38 |  |  | SPACE ONLY |  | 0 | 0 | 0 | 0
| SPACE ONLY |  |  | 39 | * | 40 |  |  | SPACE ONLY |  | 0 | 0 | 0 | 0
| SPACE ONLY |  |  | 41 | * | 42 |  |  | SPACE ONLY |  | 0 | 0 | 0 | 0
| Phase A | 4380 | VA |  |  | NOTES: |  |  | line-line voltage |  |  | 0 |  | 0
| Phase B | 4860 | VA | [5 empty] | 208 |  |  | 1
| Phase C | 4360 | VA | [5 empty] | largest motor (va)
| Total Connected | 13600 | VA | [5 empty] | 0
| load code: | ph. A | ph. B |  | ph. C |  | total | factor | calculated load (va)
| 1. LIGHTS= | 0 | 0 |  | 0 | VA | 0 | 1.25 | 0
| 2. RECEPT.= | 720 | 720 |  | 720 | VA | 2160 | 1 + 0.5 | 2160
| 3. HEATING= | 0 | 0 |  | 0 | VA | 0 | 1 | 0
| 4. KITCHEN= | 0 | 0 |  | 0 | VA | 0 | 1 | 0
| 5. EQUIP.= | 2940 | 4140 |  | 3640 | VA | 10720 | 1 | 10720
| 6. MOTORS= | 720 | 0 |  | 0 | VA | 720 | * | 720
| 7. MISC= | 0 | 0 |  | 0 | VA | 0 | 1 | 0
| (* 125% of the largest motor + 100% of the balance) | [6 empty] | TOTAL = | 13600
PANEL 'L3' | 0 | 2160 | 0 | 0 | 10720 | 720 | 0