## Sheet1
|  |  | MFIA PANEL SCHEDULE | [5 empty] | 2026-07-29 09:09 | [5 empty] | 1035 | 1370 | 1444 | Print panel schedules on stick-on | Save a panel schedule to drive A | Load a panel schedule from drive A | Load a blank 3 phase panel schedule | Load a blank 1 phase panel schedule | Print 2 panel schedules on 8.5"x11" paper | Return to Symphony menu system
| panel |  | mounting |  |  | location |  |  | connected load amps | [5 empty] | 0 | 0 | 0 |  | {SERVICES}FS{ESCAPE} | {SERVICES}FR | {SERVICES}FRPNLSCHED.WR1~ | {SERVICES}FRSINGLEP.WR1~ | pssrv1..ap47~qagpq
| PANEL 'L4' |  | FLUSH | [5 empty] | 81.4501 | [5 empty] | 2340 | 2700 | 1800
| voltage |  | phase |  |  | bus & main |  |  | calculated load amps | [5 empty] | 4860 | 2700 | 2700
| 208Y/120V |  | 3 |  |  | 225A MLO |  |  | 74.2587 | [5 empty] | 900 | 0 | 0
C | service | va | a/p | no. | a b c | no. | a/p | va | service | C |  |  |  |  | 0 | 0 | 0
1 | LIGHTING | 1035 | 20/1 | 1 | * | 2 | 20/1 | 1080 | RECEPTACLES | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0
1 | LIGHTING | 1370 | 20/1 | 3 | * | 4 | 20/1 | 900 | RECEPTACLES | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0
1 | LIGHTING | 1444 | 20/1 | 5 | * | 6 | 20/1 | 720 | RECEPTACLES | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 1200
| SPARE |  | 20/1 | 7 | * | 8 | 20/1 | 720 | RECEPTACLES | 2 | 1 | 0 | 1 | 0 | 900 | 2100 | 2060
| SPARE |  | 20/1 | 9 | * | 10 | 20/1 | 1200 | RECEPTACLES | 5 | 1 | 0 | 1 | 0 | 0 | 0 | 0
| SPARE |  | 20/1 | 11 | * | 12 | 20/1 | 1200 | RECEPTACLES | 5 | 1 | 0 | 1 | 0 | 0 | 1200 | 0
3 | RAD. HTRS., FIRE DOOR | 900 | 20/1 | 13 | * | 14 | 20/1 | 1260 | RECEPTACLES | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0
| SPARE |  | 20/1 | 15 | * | 16 | 20/1 | 1080 | RECEPTACLES | 2 | 1 | 0 | 1 | 0 | 0 | 0 | 0
2 | RECEPTACLES | 540 | 20/1 | 17 | * | 18 | 20/1 | 720 | RECEPTACLES | 2 | 1 | 0 | 1 | 0
2 | RECEPTACLES | 360 | 20/1 | 19 | * | 20 | 20/1 | 720 | RECEPTACLES | 2 | 1 | 0 | 1 | 0
2 | RECEPTACLES | 540 | 20/1 | 21 | * | 22 | 20/1 | 720 | RECEPTACLES | 2 | 1 | 0 | 1 | 0
2 | RECEPTACLES | 540 | 20/1 | 23 | * | 24 | 20/1 | 540 | RECEPTACLES | 2 | 1 | 0 | 1 | 0
2 | RECEPTACLES | 540 | 20/1 | 25 | * | 26 | 20/1 | 900 | RECEPTACLES | 5 | 1 | 0 | 1 | 0
2 | RECEPTACLES | 720 | 20/1 | 27 | * | 28 | 20/1 | 900 | RECEPTACLES | 5 | 1 | 0 | 1 | 0
5 | COPIER | 1200 | 20/1 | 29 | * | 30 | 20/1 | 720 | RECEPTACLES | 2 | 1 | 0 | 1 | 0
2 | RECEPTACLES | 720 | 20/1 | 31 | * | 32 | 20/1 | 1080 | RECEPTACLES | 2 | 1 | 0 | 1 | 0
2 | RECEPTACLES | 720 | 20/1 | 33 | * | 34 | 20/1 | 1200 | SHREDDER | 6 | 1 | 0 | 1 | 0
2 | RECEPTACLES | 720 | 20/1 | 35 | * | 36 | 20/1 | 860 | COPIER | 5 | 1 | 0 | 1 | 0
2 | RECEPTACLES | 720 | 20/1 | 37 | * | 38 |  |  | SPACE ONLY |  | 1 | 0 | 0 | 0
2 | RECEPTACLES | 720 | 20/1 | 39 | * | 40 |  |  | SPACE ONLY |  | 1 | 0 | 0 | 0
| SPARE |  | 20/1 | 41 | * | 42 |  |  | SPACE ONLY |  | 1 | 0 | 0 | 0
| Phase A | 10035 | VA |  |  | NOTES: |  |  | line-line voltage |  |  | 0 |  | 0
| Phase B | 10070 | VA | [5 empty] | 208 |  |  | 1
| Phase C | 9204 | VA | [5 empty] | largest motor (va)
| Total Connected | 29309 | VA | [5 empty] | 0
| load code: | ph. A | ph. B |  | ph. C |  | total | factor | calculated load (va)
| 1. LIGHTS= | 1035 | 1370 |  | 1444 | VA | 3849 | 1.25 | 4811.25
| 2. RECEPT.= | 7200 | 5400 |  | 4500 | VA | 17100 | 1 + 0.5 | 13550
| 3. HEATING= | 900 | 0 |  | 0 | VA | 900 | 1 | 900
| 4. KITCHEN= | 0 | 0 |  | 0 | VA | 0 | 1 | 0
| 5. EQUIP.= | 900 | 2100 |  | 3260 | VA | 6260 | 1 | 6260
| 6. MOTORS= | 0 | 1200 |  | 0 | VA | 1200 | * | 1200
| 7. MISC= | 0 | 0 |  | 0 | VA | 0 | 1 | 0
| (* 125% of the largest motor + 100% of the balance) | [6 empty] | TOTAL = | 26721.25
PANEL 'L4' | 3849 | 17100 | 900 | 0 | 6260 | 1200 | 0